ITEM NO. 13 (B-30)

1.	Name of Work: Purchase of Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV.

2.	Department 	: 	ELECTRICITY DEPARTMENT

3.	Brief History of the Proposal: A case for purchase of 37 Nos. Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV was processed against the sanctioned estimate amounting to Rs.17,49,37,148/- duly approved by council vide Reso. No.21 (B-21) dt.17.12.08 in compliance to DERC guidelines that the oil type transformers in the Electric Substation installed inside the main buildings are required to be replaced with dry type transformers.

4. 	Detailed Proposal of the Subject: Tenders were invited in three cover system from only manufacturers through e-procurement system for the purchase of 37 Nos. Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV by giving due publicity to the tender as per the codal provisions. In response to the Tender Enquiry, offers of the following three firms were received on due date of opening i.e.29.07.09.

- M/S Voltamp Transformers Ltd.

- M/S Ames Impex Electricals Pvt. Ltd.

- M/s Vijai Electrical Ltd.

The offers of the above firms were scrutinized and subsequently examined by the Planning Division and after due approval the price bids of all the three eligible firms were opened on 02.09.09. The detailed position of the firms explained below:-

| S.No. | Description of Item | Name of Tenderer |  |  |
| --- | --- | --- | --- | --- |
| 1. | 1600 KVA, 10.5/0.415 KV Distribution Transformer Dry Type (Resin Cast) Qty=37 Nos. | M/s Voltamp Trf. Ltd. | M/s AMES Impex Electrical Pvt. Ltd. | M/sVijai Electricals Ltd. |
| 2. | Basic Rate for Unit Transformer | Rs.15,86,000.00 | Rs.12,60,000.00 | Rs.20,43,000.00 |
| 3. | Price | Firm | Firm | Variable with + 10% ceiling i.e. Rs.20,433 |
| 4. | Excise Duty @ 8.24% | Rs.1,30,686.40 | Rs.1,03,824.00 | Rs.1,85,177.52 |
| 5. | Present Rate of CST @ 2% | Rs.34,333.728 | Rs.27,276.48 | Rs.48,649.55 |
| 6. | Freight | Rs.12,500.00 | Rs.20,000.00 | Rs.23,250.00 |
| 7. | Insurance | Rs.5,500.00 | Rs.1,890.00 | Rs.6,860.00 |
| 8. | Packing | NIL | NIL | NIL |
| 9. | Handling | NIL | NIL | NIL |
| 10. | Computed Unit Price | Rs.17,69,020.128 | Rs.14,12,990.48 | Rs.25,11,237.07 |

Based on the computed cost of the each tendering firm, capitalized cost has been worked out to evaluate the position of lowest tendering firm as per the provision in the NIT as detailed below:-

Capitalized Cost - Comparison Chart

| Name of the Firm | Computed Unit Rates | No Load Losses | Load Losses | Capitalized unit price | Capitalized Cost for 37 Nos. Trf. |
| --- | --- | --- | --- | --- | --- |
| M/s Voltamp Transformers Ltd. | Rs.17,69,020.128 | 3.25 KW | 9.95 KW | Rs.73,41,971.21 | Rs.12,36,52,934.77 |
| M/s Ames Impex Electricals Pvt. Ltd | Rs.14,12,990.48 | 3.0 KW | 14.0 KW | Rs.32,87,827.58 | Rs.12,16,49,620.46 |
| M/s Vijai Electricals Ltd. | Rs.25,11,237.07 | 2.4 KW | 8.4 KW | Rs.37,65,213.55 | Rs.13,93,12,901.35 |

M/s. Ames Impex Electricals Pvt. Ltd. emerged as the lowest tendering firm with their quoted basic rate Rs.12,60,000.00 (Ex works) plus Excise duty @ 8.24%, CST @ 2%, Freight Rs.20,000.00 per transformer & Insurance Rs. 1,890.00 per transformer. The computed unit price of transformer works out to Rs.14,12,990.48. The total computed cost for the purchase of 37 No. transformer has been worked out to Rs.5,22,80,647.76.

Ex-works unit rates of the lowest tenderer are 29.62% below NIT estimated cost. These rates are 24.32% below the justified rates based on the supply orders of M/s Tata Project Ltd.

The case was again examined by the Planning and subsequently examined & concurred by Finance vide diary No. R-75/PS/FA/10 Dt. 08.02.10 for the above purchase.

5.	Financial Implications: Rs.5,22,80,648.00/- (Rs. Five crore twenty two lacs eighty thousand six hundred fourty eight rupees only), inclusive of all prevalent taxes, duties, freight, insurance, packing & handling.

6.     	Implementation Schedule: Commencing with 10 Nos. within three months and completion @ 9 Nos. per month thereafter and completion in six months from the date of approval of drawings to be submitted with in 15 days from the date of issue of supply order.

- Comments of the Finance Department : Finance vide diary No. R-75/PS/FA/10 Dt. 08.02.10 has seen and concurred with no comments.

8.	Comments of the Department on comments of Finance Deptt. :	Nil

9.	Legal Implication of the Subject: 		Nil

10.	Details of previous Council Resolution:	Nil

11.	Comments of Law Department:		Nil

12.	Comments of the department on the comments of Law Department:	 	Nil

13.	Certification by the Department:

All Central Vigilance Commission (CVC) guidelines have been followed.

14.	Recommendations of the Department: The case may be placed before the Council for the purchase of 37Nos. Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV from the lowest tendering firm M/s. Ames Impex Electricals Pvt. Ltd. with their quoted unit rate of Rs.12,60,000.00 (Ex works) plus Excise duty @ 8.24%, CST @ 2%, Freight Rs.20,000.00 & Insurance Rs. 1,890.00 and at the total computed cost of Rs.5,22,80,648.00 on the terms, conditions and specifications of NIT. Since the material requirement is of urgent nature, approval may also be accorded to place Supply Order on the firm in anticipation of the confirmation of the minutes of the Council meeting.

15.	Draft Resolution: Resolved by the Council that the approval is accorded to the purchase of 37Nos. Distribution Transformers 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV from lowest tendering firm M/s. Ames Impex Electricals Pvt. Ltd. with their quoted unit rate of Rs.12,60,000.00 (Ex works) plus Excise duty @ 8.24%, CST @ 2%, Freight Rs.20,000.00 & Insurance Rs.1,890.00 and at the total computed cost of Rs.5,22,80,648.00 on the terms, conditions and specifications of NIT. Approval is also accorded to place Supply Order on the firm in anticipation of the confirmation of the minutes of the Council meeting.

COUNCIL’S DECISION

Resolved by the Council to accord approval for purchasing of 37Nos. Distribution Transformers of 1600KVA Dry Type (Cast Resin) 10.5/0.415 KV, from lowest tendering firm M/s. Ames Impex Electricals Pvt. Ltd., with their quoted unit rate of Rs.12,60,000.00 (Ex works) plus Excise duty @ 8.24%, CST @ 2%, Freight Rs.20,000.00 & Insurance Rs.1,890.00 and at total computed cost of Rs.5,22,80,648.00 on the terms, conditions and specifications of NIT.

It was also resolved that further action may be taken by the Department in anticipation of confirmation of the Minutes by the Council.