ITEM NO. 13 (B-18)

(1) 	Name of the work :	Construction of 11 KV Electric Substation behind Hanuman Mandir, Hanuman Lane, New Delhi.

(2) 	Name of the Department  :  Electricity

(3) 	Brief History of the case :

There are various proposals for construction of a large number of multi storied flats in DIZ area Gole Market area in place of existing dilapidated government quarters and barracks.  Many private multi storied buildings are likely to come up in Connaught Place and adjoining area.  Railways have an ambitious plan for upgradation of New Delhi Railway Station requiring huge power demand.  The Central Govt. has also plans to construct various residential/cultural/office complexes in NDMC area.  NDMC is also planning to construct certain residential/commercial buildings  besides rejuvenation of markets in its area.  The power requirement will also increase due to increasing alternation and computerization of all economic activities.  The present power infrastructure is inadequate even to meet the present load requirement and therefore, to meet the existing requirement as well as future load requirement, the infrastructure is required to be created/augmented for which various Sub-stations of 220 KV, 66 KV, 33 KV & 11 KV have to be established keeping in view the short term and long term requirements.  A team of our senior officers had observed during their visit to Japan recently that Ginza area of Tokyo City, which is almost the same size of NDMC, had  power consumption of 2000 MVA.  We can expect demand of NDMC area to go up and come upto the level of Ginza in the next one or two decades, alongwith the economic growth and enhancement of standard of living.  After that a number of correspondences have been made by the Chairman, E-in-C, C.E.(E), S.E.(E) & E. E.(E)(P.11KV).

Out of 81 sites, 24 sites were identified for Electric Substations by joint survey by NDMC/L&DO staff .  Some sites have been allotted by L&DO in which this site under consideration is also included.

A plot for establishing an Electric Substation having 2 x 1000 KVA transformers behind Hanuman Mandir, Hanuman Lane has been allotted by L&DO.  The drawing of the same has also been prepared by C.A., NDMC.  This proposed Sub-station would conceptually be a local  distribution Sub-station as well as a switching station as an extension to the 33 KV Hanuman Road Sub-station.

(4)  	Detailed proposal on the Project :

The following cables have been proposed :

- 2 x 400 sq.mm 11 KV XLPE cable has been proposed from Sub-station Hanuman Road as incomer.

- 2 x 400 sq.mm 11 KV XLPE cable has been proposed from Sub-station Raja Bazar as second incomer.

- 1 x 400 sq.mm 11 KV XLPE shall be provided as outgoing to Sub-station Mohan Singh Place.

- 1 x 400 sq.mm 11 KV XLPE shall be provided as outgoing to Sub-station Shaheed Bhagat Singh Marg.

(e)	Earlier an estimate was issued for laying 1 x 400 sq.mm cable from Sub-station Regal to Sub-station Mohan Singh Place via Sub-station Standard Restaurant and Sub-station Khadi Gram Udyog {This estimate is being executed by E.E.(C-II) }.  Now it has been proposed that instead of terminating that cable in Sub-station Mohan Singh Place the same shall be terminated in the proposed Sub-station Hanuman Lane (behind Hanuman Mandir).  A straight through joint has been proposed outside the Sub-station Mohan Singh Place for this purpose.   This estimate of proposed Sub-station at Hanuman Mandir shall be issued to E.E.(C-II) to incorporate the changes while executing both the estimates.

One HT panel shall become spare at Electric Substation Mohan Singh Place after disconnecting the interconnector between Palika Kendra and Mohan Singh Place.  This spare HT panel at Mohan Singh Place shall be utilized to connect HT feed 1 x 400 sq.mm 11 KV  XLPE coming from the proposed 11 KV feed from Electric Substation Hanuman Lane (Behind Hanuman Mandir).  It has been agreed that  2 x 1000 KVA oil type transformer shall be installed out of the transformers which would be spare after replacement/ augmentation of oil type transformer with dry type transformer (Phase-II).  50% cost of new transformer as indicative cost has been taken in this estimate on account of providing old dismantled transformer.  Existing HT cable from Sub-station Mohan Singh Place to Sub-station Palika Kendra shall be dismantled to the extent economical and credit shall be afforded to Municipal Revenue.

(5)	Financial implications : Financial implications in the proposal is anticipated to be Rs. 1,80,28,500/-.

(6)	Implementation schedule: 06 months

(7)	Comments of the Finance Deptt. on the subject :

Finance Deptt. vide Dy. No. 1840/Finance/R-Elect. dated 26-8-09 has concurred in the  estimate amounting to Rs.1,80,28,500/- for Construction of 11 KV Electric Substation behind Hanuman Mandir, Hanuman Lane, New Delhi subject to the following  :

- Availability of funds.

- Approval of competent authority.

- Codal provision and CVC guidelines must be adhered to.

- Correctness of information, data and computation must be ensured and certified.

- The estimate file be given page numbers.

- Comments of the Deptt.

- A  suitable provision in the Budget Head E-4-1 will be kept in R.E. 2009-10.

- Approval of competent authority i.e. Council is being obtained.

- All  codal provisions and CVC guidelines have been adhered to.

- The information and data submitted have been verified.

- Needful has been done.

(9)	Legal implication of the Project : - No legal implication is involved.

(10)	Details of previous Council Resolution :	NIL

(11)	Comments of  Law Deptt. :  Law Deptt. has commented that “No legal implication/issue is involved at this stage in the Agenda item.  This has concurrence of Law Deptt..”

(12)	Comments of the Deptt. on the comments of Law Deptt. :  N.A.

(13)	Certification by the Deptt. that all Central Vigilance Commission (CVC) guidelines have been followed : It is certified that all Central Vigilance Commission (CVC) guidelines have been followed in processing the case.

(14)	Recommendation of the Deptt. : The estimate amounting to Rs.1,80,28,500/-  for Construction of 11 KV Electric Substation behind Hanuman Mandir, Hanuman Lane, New Delhi  may be placed before the Council to accord administrative approval and expenditure sanction.  Since the work is of urgent nature, approval is solicited to take further action in anticipation to confirmation of the Minutes of Council Meeting.

(15)	Draft Resolution : Resolved by the Council that Administrative approval and expenditure sanction is granted to the estimate amounting to Rs.1,80,28,500/- for Construction of 11 KV Electric Substation behind Hanuman Mandir, Hanuman Lane, New Delhi.  Further approval is accorded to take further action in anticipation to confirmation of the Minutes of Council Meeting.

COUNCIL’S DECISION

Resolved by the Council to accord administrative approval and expenditure sanction to the estimate amounting to Rs.1,80,28,500/- for Construction of 11 KV Electric Substation behind Hanuman Mandir, Hanuman Lane, New Delhi.

It was also resolved that further action in the matter be taken in anticipation of confirmation of the minutes by the Council.