Item No. 2 (B-14)

1.	Name of the Subject:       	Air Conditioning of Palika Kendra Building.

Sub-Head :  Supplying, installation, testing & 					commissioning of 410 T.R. capacity screw type 					chiller 	with the existing HVAC system of 						Palika 	Kendra Building.

2.	Name of the Department :     Electricity Department.

3.	Brief History of the subject:    The existing HVAC system installed by M/S. Voltas 	Ltd. at Palika Kendra is working since 1984 and has already outlived its prescribed 	useful life of 15 years. Since this was not giving the desired AC affect in the building, 	technical study of the entire air-conditioning system and its requirement was carried 	out by M/s. Voltas Ltd. and their report was also accepted by the Chairperson, NDMC. 	Certain improvements were suggested by M/s. Voltas Ltd. in the existing system 	which are being/have been carried out. Installation of one additional 410 T.R. screw 	type chiller was suggested in the first phase by M/s. Voltas Ltd. with the existing 	HVAC system at Palika Kendra building.

4.	Detailed proposal on the subject/project:    The technical study report of the 	central AC plant was submitted by M/s. Voltas Ltd. on 28.11.05  and the same was 	accepted by the Chairperson, NDMC on 23.1.06. The works recommended in the 	technical study report shall be got done in three phases as the building is fully 	occupied. Once the proposed 410 screw type chiller is installed, the same will take 	core AC load of the building and the AC affect shall be to a comfortable level,. The 	existing AC plant shall thereafter be replaced – 2 to 3 at a time with another 410 TR 	screw type chiller. So ultimately, all the six existing AC plant shall be replaced and the 	total capacity of the new AC plant shall be 3x410 i.e. 1230 TR. For the time being, 	the proposal has been made to install only one additional 410 TR screw type chiller. 	The total air-conditioning load of the building including proposed additions / 	alterations in the Palika Kendra building from ground floor to 3rd floor has been 	assessed to be 950 TR by M/s. Voltas Ltd. against which the existing capacity 	available is only about 400 TR

5.	Financial implications:        Rs. 82.75 lac.

6.	Implementation Schedule:   Works may be executed in six to eight months after 	the award of work.

7.	Comments of Finance Department:   Finance department have concurred in the 	estimate amounting to Rs. 82.75 lacs vide thier diary No. FA-2788 Dated 7.12.06 	subject to following:

  - Approval of competent authority.

  - Availability of funds.

  - The Work would be done after adhering the codal provisions.

  - Certification by the department that estimate has been prepared strictly on the basis 	of report of M/s. Voltas Ltd.

8.	Comments of the department on the comments of Finance Department:

    - Approval of the competent authority is being sought.

    - Funds are available.

- Work will be got done/executed by adhering the codal formalities.

- Certified that the estimate has been prepared on the basis of report of M/s. Voltas 	Ltd.

9.	Recommendations:	The estimate is placed before the Council for consideration 	and according administrative approval and expenditure sanctioned to the estimate 	amounting to Rs. 82.75 lacs for the above works as per the  concurrence of  Finance 	Deptt.. The works are expected to be completed by December,2007.

COUNCIL’S DECISION

Resolved by the Council that administrative approval and expenditure sanction to the estimate amounting to Rs.82.75 lacs is accorded for supplying, installation, testing & commissioning of 410 TR capacity screw type chiller with the existing HVAC system of Palika Kendra Building.

Further resolved by the Council that further no new window/split AC will be sanctioned for the Palika Kendra Building.