ITEM NO. 05 (B-08)

- Name of Subject / Project:-

Replacement of 33KV SF6 Panel board with 33KV GIS DBB panel board at 33KV ESS School Lane.

- Name of the Department/Department concerned:-

ELECTRICITY DEPARTMENT

- Brief History of the Subject/Project:-

The existing 33KV, SF6 type 9 panels (Kirloskar make) boards were installed in the year 1991 at ESS School lane. The manufacturer has now upgrade the design of their panel and stopped manufacturing of this type/model of SF6 DBB Panels. Spare parts of these obsolete models are also not available with the manufacturing firm and as such the department is in difficulty in managing the spare part which ultimately affect the repair work and in restoration of power supply.  These Panels also have served 21 years in lieu of useful prescribed life of 25 years.  Besides above, presently frequent fault at this ESS in the switchgear panel have been recorded which causes interruption of power supply in the sensitive area of NDMC. Due to disruption in operation, these panels are un-reliable. It is therefore felt that these panels should be replaced with latest GIS panel which is almost maintenance free panel. Keeping in view of above difficulties, M/S PGCIL has installed GIS Panel in NDMC system and NDMC of its own also installed the same GIS panel for maintaining the uniformity in the system.

- Detailed Proposal on the Subject/Project:-

In order to improve the reliability of power supply in adjoining area by providing latest technology based equipment which is almost maintenance free and strengthen power supply network in NDMC area.

In the proposed estimate, two No. additional panels i.e. two Nos. Bus – Section have been considered to utilize the panel board independently being a double bus bar panel board.

The proposed 33KV GIS DBB board is having provision to terminate 2x3cx400sqmm, XLPE cable in single unit comprising of 15 panels with its C&R Board at ESS School Lane.  Accordingly, PE has been framed based on approved rate/SIR/Market rates.

- Financial Implications of the proposed Project/Subject:-

`749.76 Lacs including 3% contingencies. The expenditure shall be charged to the Budget Head Chart of A/C 81/490/90/12 and field code 209 for which a budget provision of `10 Lacs has been kept in BE 2012-13 and balance amount shall be kept in RE 2012-13.

- Implementation schedule with timeliness for each stage including internal processing:-

The scheme will be executed within 24 months & shall be executed through call of tender and partially by department.

- Comments of the Finance Department on the subject:-

The finance Deptt. has concurred the estimate vide diary No. 772/Finance/R-Elect. Dt. 03.04.12 subject to the entry of dismantled panels may be  made in the dismantled register and the re-utilization of the same be ensured in future in other 33KV ESS i.e. Dalhousie Road, Scindia House and National Archives where same make panels are installed.

- Comments of the Department on comments of Finance Deptt:-

At present, 33KV, 9 panel SF6 DBB Board of Kirloskar make is installed at ESS School Lane. Out of these 9 Panels, there have been faults in 5 Panels and are not reliable. The remaining 4 Panels shall be utilized at other 33KV ESS at Dalhousie Road, Scindia House and National Archives where same make of panels are installed. Further , 02 more additional Panels are required at ESS School Lane, one for feeding the proposed 33KV ESS at Janpath Lane and the other as an inter-connector between 220KV ESS at Harish Chander Mathur Lane and 66KV ESS School. The replacement of 9 Panels of Kirloskar make switchboard is proposed to be done with 15 Panel GIS switchgear which is practically maintenance free and compact in size.

- Final views of Finance Department:-

The finance Deptt. has concurred the estimate vide diary No. 981/Finance/R-Elect. Dt. 19.04.12.subject to the proposal may also be shown to the Advisor (Power), in order to ensure that the same is in order, before processing the case further for seeking approval of competent authority.

Comments of the department: - The proposal has been shown to Advisor (Power) and he has considered the proposal of 15 GIS panels including 2 Nos. bus section to be in order.

- Legal implications of the Subject/Project: -

Nil

- Details of Previous Council Resolution, existing law of Parliament and Assembly on the subject:-

Nil

- Comments of the Department on the comments of Law Deptt:-

Nil

- Final view of Law Deptt [wherever necessary]:-

Has no legal issue.

- Certificate that all Central Vigilance Commission’s guidelines have b een followed while processing the case:-

All CVC guidelines shall be adhered at the time of award of work for implementing the scheme.

- Recommendation:-

As per final view of Finance Department the case has been shown to Advisor (Power) and same has been considered in order.

The estimate amounting to `749.76 Lacs for Replacement of 33KV SF6 Panel board with 33KV GIS DBB 15 panel board with provision of termination of double cable of 3CX400sqmm, XLPE with its C&R Panel at 33KV ESS School Lane may be placed before the Council to accord Administrative Approval and Expenditure Sanction.

- Draft Resolution:-

Resolved by the Council that Administrative Approval & Expenditure Sanction is granted to the estimate amounting to `749.76 Lacs for Replacement of 33KV SF6 Panel board with 33KV GIS DBB 15 panel board with provision of termination of double cable of 3CX400sqmm, XLPE with its C&R Panel at 33KV ESS School Lane.

COUNCIL’S DECISION

Resolved by the Council that Administrative Approval & Expenditure Sanction is granted to the estimate amounting to `749.76 Lacs for “Replacement of 33KV SF6 Panel Board with 33KV GIS DBB 15 panel board with provision of termination of double cable of 3CX400sqmm, XLPE with its C&R Panel at 33KV ESS School Lane”.