ITEM NO. 08 (A-21)

1. 	NAME OF THE SUBJECT	:	Replacement of Municipal Water Mains in NDMC Area (SH Replacement of 450mm dia water mains along Tilak Marg from Sikandra Road to UGR at Tilak Lane Boosting Station).

2.	NAME OF THE DEPARTMENT	:	Civil Engineering Department (Water Supply Division).

3. 	BRIEF HISTORY OF THE SUBJECT:-

One of the sources of water to NDMC area is from the tapping at Hans Bhawan from the Delhi Jal Board water mains coming from Wazirabad Water Works. The water from this tapping is feeding the UGR at Tilak Lane & Bengali Market. The feeder line consisting of 450mm dia pre-stressed concrete is running along the footpath of Tilak Marg from Sikandara Road end to Tilak Lane & was laid in the year 1988-89 which feeds the UGR round the clock with water under great pressure. Due to the passage of time i.e. about 23 years the line has developed leakages at several places & is presently leaking at more than 11 places within a short span of 20 to 25 metres & at more than 5 to 6 places in a span of 10 to 15 metres. The condition of this line is pathetic & is deteriorating day by day. The repairs of this PSC Line is also difficult due to its weak strength. Regular complaints of continuous leakage of water in the service road of Tilak Marg are being received.

Accordingly, the P.E. amounting to ` 1.80 crores is prepared for laying the D.I. Pipeline of 450mm dia by cut & cover method under the footpath & by MS Pipe through trenchless method for crossing of the main roads. The provision for the sluice valves, air relief valves, brick masonry chambers have been taken in the estimate.

4. 	DETAILED PROPOSAL OF THE SUBJECT:-

Since the PSC Pipeline has become obsolete & its condition is deteriorating day by day it is proposed to lay a 450mm dia D.I. Pipeline from the Sikandara Road end along Tilak Marg to Tilak Lane UGR near Police Station Tilak Marg & the MS Pipeline shall be laid by trenchless method for crossing of the main roads. This shall be the replacement of the old damaged PSC Line of 450mm dia feeding the UGR of Tilak Lane from the Sikandara Road end which has become unserviceable. This line is running round the clock & under heavy pressure. Considering the existing (pathetic) condition of PSC Pipe, the only solution is that the line should be replaced to avoid not even wastage of precious water but also to prevent contamination & disruption of supply. The scrap value of the old PSC Pipeline shall be negligible as compared to the cost of excavating, dismantling, disposing & restoring the surface of footpath / cycle track so the cost of dismantled material may be treated as nil.

5.	FINANCIAL IMPLICATIONS OF THE PROPOSED SUBJECT:-

The estimated cost of the work including the R.R. Charges, etc. is about ` 1.80 crores for which the A/A & E/S is to be accorded.

6.	IMPLEMENTATION SCHEDULE WITH TIME LIMITS FOR EACH STAGE INCLUDING INTERNAL PRCESSING:-

Detailed Estimate		-	One Month.

NIT & Approval		-	Three Months.

Execution 			-	Four Months.

7.	COMMENTS OF FINANACE DEPARTMENT ON THE SUBJECT:-

Finance has concurred the proposal for the Preliminary Estimate amounting to Rs.1,79,30,500/- (Rupees One Crore Seventy Nine Lacs Thirty Thousand & Five Hundred Only), duly checked by Planning against the proposed HOA 51-490-90-21 for which availability of funds may be ensured before incurring any liability. However, department may ensure & certify that replacement of whole line is essentially required and pipelines proposed for replacement have outlived its life.

8.	COMMENTS OF THE DEPARTMENT ON THE COMMENTS OF FINANACE DEPARTMENT:-

Finance Department has concurred in the proposal. It is to ensure that adequate budge will be sought in R.E. It is also to certify that the old line has outlived its life & need immediate replacement.

9.	LEGAL IMPLICATION OF THE SUBJECT:-

No Law Point.

10.	DETAILS OF PREVIOUS COUNCIL RESOLUTIONS, EXISTING LAW OF PARLIAMENT AND ASSEMBLY ON THE SUBJECT:-

Nil

11.	COMMENTS OF THE LAW DEPARTMENT ON THE SUBJECT:-

Nil

12.	COMMENTS OF THE DEPARTMENT ON THE COMMENTS OF LAW DEPARTMENT:-

No Comments.

13.	CERTIFICATION BY THE DEPARTMENT THAT ALL CVC GUIDELINES HAVE BEEN FOLLOWED WHILE PROCESSING THE CASE:-

It is certified that all CVC Guidelines have been followed while processing the case.

14.	RECOMMENDATION:-

The above said proposal is recommended for approval since it is the most economical & effective one to the  old pipeline of 450mm dia along Tilak Marg with D.I. Pipe of 450mm dia D.I. Fitting & MS Pipe for trenchless work so as to keep the source of water to NDMC Area in a sturdy position and also to prevent wastage & contamination of precious water. The preliminary Estimate amounting to Rs. 1,79,30,500.00 (Rupees One Crore Seventy Nine Lacs Thirty Thousand & Five Hundred Only).

COUNCIL’S DECISION

Resolved by the Council to accord administrative approval and expenditure sanction to the preliminary estimate amounting to Rs.1,79,30,500/- for work of Replacement of Municipal Water Mains in NDMC Area (SH Replacement of 450mm dia water mains along Tilak Marg from Sikandra Road to UGR at Tilak Lane Boosting Station).

It was further directed by the Council that henceforth life of the existing pipeline and one proposed to be laid should also be indicated in the proposal.