ITEM NO. 03 (B-11)

- Name of the work:   Installation of 2 x 990 KVA Unitized Substation at XY Block, Sarojini Nagar.

- Name of the Department: 	Electricity

- Brief History of the case :

A meeting was held in the chamber of C.E.(E-II) on dated 21/06/2010 in the presence of S.E.(E-II) , EE(D/S) and EE(P-11KV). It has been proposed to install 2 x 990 KVA Unitized Sub Station for Palika Gram NDMC flats XY Block, Y Block, YZ and Z Block at Sarojini Nagar area, as load demand has increased in these areas. The estimate was sent to Advisor (Electric) who suggested some amendments in the estimates and the same have been incorporated to improve reliability and feasibility.

- Detailed Proposal on the project:-

- Existing HT Cable 1 x 400 Sqmm /3C between Sub Station Trauma Centre and Sub Station Nursing Hostel is proposed to LILO at Sub Station Safdarjung Staff Qtrs. No. 2.

- An additional HT cable of 1X400 Sqmm/3C between Sub Station Trauma Centre and Sub Station Safdarjung Staff Quarter No.02 shall be proposed and shall be connected in the same HT panel where existing HT cable 1X400Sqmm/3C between Trauma Centre to Nursing Hostel is proposed to LILO at Sub Station Safdarjang Staff Qtr. No. 02.

- Interconnector between Sub Stations Safdarjung Staff Qtr. No. 01 to Sub Station Safdarjung Staff Qtr. No. 02 is proposed to be augmented from proposed 1 X400Sqmm/3C to 2X400Sqmm/3C and existing interconnector of 1X150Sqmm/3C between two Sub Stations may be utilized for setting up a Unitized Sub Station in this area to meet the future growth of load instead of dismantling the cable as proposed by Advisor(Electric). Separate estimate shall be prepared for unitized Sub Station.

- The proposed 1x 400 Sqmm /3c HT Cable from Sub Station  Safdarjung Staff Qtrs. No. 2 to Unitized Sub Station to be installed at Palika Gram NDMC Flats XY Block. This HT feed shall be extended to second Unitized Sub Station 1 x 990 KVA to be installed at YZ Block. This HT feed 1 x 400 Sqmm/3C from second Unitized Sub Station shall be further extended to proposed Sub Station Cross Road No. 2. The positions of two no. Unitized Sub Stations shall be decided with the consent of EE (M/S) and EE (D/S).

- Two No. HT panels 400Amp VCB type, O/G  and one No. I/c HT panel VCB, 400Amp. shall be installed at Sub Station Safdarjung Staff Qtrs, No. 2.

- 1 No. HT Panel VCB type, O/G shall be installed at Sub Station Cross Road No. 2 for Unitized Sub-station at YZ Block .

- 4 No. G. S. pillars Big size shall be installed in the adjoining areas of XY and YZ blocks having their locations with the consent of EE (D/S) and EE (M/S).

- Financial Implications:

Estimate is anticipated to have fianncial implication of Rs. 1,82,99,000/-

- Implementation schedule : 		Eight months

- Comments of the Finance Department on the subject: Finance Department vide Dy. No. 996/Finance/ R-Elect dt. 14.06.11 have concurred in the estimate with no further comments.

- Comments of the Department on the commets of the Finance Department:  		NIL.

- Legal Implication of the project:  No legal implication is involved.

- Details of previous Council Resolution :  NIL, new case.

- Comments of Law Department:  	It has no legal issue.

- Comments of the Department on the comments of Law Department :   Nil

- Certification by the Department that all Central Vigilance Commission (CVC) guidelines have been followed:  It is certified that all Central Vigilance Commission (CVC), guidelines have been followed in processing the case.

- Recommendation:  The estimate amouting to Rs. 1,82,99,000/- for installation of 2X990 KVA Unitized Sub Stations at XY- Block, Sarojini Nagar may be placed before the council to accordAdministrative Approval and Expenditure Sanction. Approval may also be accorded to take further action in anticipation to confirmation of the minutes of Council Meeting.

- Draft Resolution: Resolved by the council that Administrative Approval and Expenditure Sanction is granted to the estimate amounting to Rs. 1,82,99,000/- for installation of 2X990 KVA Unitized Sub Stations at XY-Block, Sarojini Nagar. Approval is also accorded to take further action in anticipation of confirmation of the Minutes of the Council Meeting.

COUNCIL’S DECISION

Resolved by the Council to accord administrative approval and expenditure sanction to the estimate amounting to Rs.1,82,99,000/- for installation of 2X990 KVA Unitized Sub Stations at
XY-Block, Sarojini Nagar.

It was also resolved that further action may be taken by the Department in anticipation of confirmation of the minutes by the Council.