ITEM NO. 16 (B-27)

- Name of work-  Establishing 33KV S/S at Keventer Dairy

- Name of the Department- ELECTRICITY DEPARTMENT

- Brief history of the proposals-

The load of State Guest Houses, Hotels, and important embassies like U.S.A., Australia, U.K., China among others is being met from ESS Nehru Park, Bapu Dham and Race Course Road. These ESS are already loaded to their maximum capacities. In case of outage at any of this ESS the whole system is put under constraints. Further the load of the Embassies, State Guest House and other buildings in the area is increasing day by day. It is therefore, essentially required to establish a 33KV ESS at the proposed site which will cater to the load demand of Embassies , State Guest House, Diplomatic Enclave and part of President Estate. The establishment of this ESS will relieve the load on above referred ESS, thus strengthening the electrical system in the area and making it more reliable.

The land for construction of 33KV ESS has already been allotted to NDMC by L&DO. This scheme is a part of Xth five year plan which has been technically cleared by CEA vide No. DPD/UT/312(DEL)/2003/419 dated. 15.12.03.

The Estimate has been seen by Advisor (Elect.) & Advisor (Power) and concurred by the Finance Deptt.

- Detailed proposal on the Project-

To meet the load demand of the area following has been proposed in the estimate.

- 16/20MVA, 33/11KV Pr. Transformer 				- 2Nos.

- 33KV, 1250 A, 1500 MVA, SBB Indoor Type GIS 7 Panel Board  	 -1 No.

- 11KV, 1250 A, 350 MVA, DBB Indoor Type SF-6/VCB 13 Panel Board -1 No

- 11KV, 1250 A, 350 MVA, SBB Indoor Type SF-6/VCB 11 Panel Board -1 No

- Distribution Transformer 1000KVA, Oil Type, 10.5/0.415 KV rating      -2 Nos.

- 11KV, 5.04MVAr Capacitor Bank				-2Nos.

- The S/S is proposed to be fed through 33KV, 3x400 Sq.mm XLPE Cable from 66KV S/S  Bapu Dham   and 66KV S/S State Guest House.

Accordingly an estimate amounting to Rs. 1291.64 Lacs including 3% contingencies has been prepared to cover the cost of the above work including the cost of the building and allied works.

- Financial Implications- The estimated cost for establishing 33KV S/S at Keventer Dairy is Rs. 1291.64 Lacs chargeable to the head of a/c E.4.1.

- Implementation schedule with timeliness for each stage including internal processing: - The scheme has been outsourced to M/s Power Grid Corporation of India Limited for turnkey execution and as per MOU completion time is 24-30 months.

- Comments of the Finance Department on the subject- The finance Deptt. vide Diary No. 2446/Finance Dated 16.11.09 has concurred in the preliminary estimate amounting to Rs. 1291.64 and offer no further comments.

8.	 Comments of the Department on comments of Finance Deptt:  Nil

- Legal implications of the Project: -  			Nil

- Details of Previous Council Resolution- 		Nil

- Comments of the Law Deptt. on the Project: - 	Nil

- Comments of the Deptt. on the Law Deptt:-   	Nil

- Certificate on CVC guidelines:-  All CVC guidelines shall be adhered to while processing the case.

- Recommendation:- The preliminary estimate amounting to Rs. 1291.64 Lacs for establishing 33KV ESS at Keventer Dairy, may be placed before the Council to accord administrative approval and expenditure sanction. Since the work is of urgent nature, approval may also be solicited to take further action in anticipation to confirmation of the Minutes of Council Meeting.

- Draft Resolution:- Resolved by the Council that Administrative approval & expenditure sanction is granted to the preliminary  estimate amounting to Rs. 1291.64 Lacs for establishing 33KV Electric Sub-Station at Keventer Dairy. Further approval is accorded to take action in anticipation to confirmation of the Minutes of Council Meeting.

COUNCIL’S DECISION

Resolved by the Council to accord Administrative approval & expenditure sanction to the preliminary  estimate amounting to Rs.1291.64 Lacs for establishing 33KV Electric Sub-Station at Keventer Dairy.

It was further resolved that Department may initiate action in anticipation of confirmation of the minutes by the Council.