ITEM NO. 02 (B-01)

(1) Name of the work :	Shifting of Existing sub-station from ground floor to the proposed location in  basement of Handloom Complex at Janpath Lane,  New Delhi

(2) Name of the Department  :  Electricity

(3) Brief History of the case :

SEE, DCEC VIII, CPWD,IP Bhawan, New Delhi has requested for removal/shifting of 2 nos. transformers and sub-station from Handloom Complex at Janpath Lane, New Delhi for construction of multi- storey building for Handloom Complex. The then C.E.(E)  has mentioned on the PUC that they should be asked to keep provision of sub-station in the proposed new building of Handloom House.

Accordingly he was requested to provide sub-station space for  shifting of existing sub-station  at Janpath Lane. Sr. Architect CPWD submitted two sets of drawings on 16.10.10 in respect of construction of Handloom Marketing complex at Janpath. In this connection a meeting was held in the chamber of Chairman on 08.10.08 with the consumer wherein they  agreed to  provide space for 33 KV electric sub-station. They have also provided the space for NDMC 11 KV electric sub-station in the area allocated in the basement which is acceptable.

C.E.(E) II has accorded the approval on date 12/07/09 to frame the estimate for shifting of existing sub-station from ground floor to proposed location in the basement of Handloom Complex at Janpath.

(4)  Detailed proposal on the Project :

Part ‘A’

- One no. 1600 KVA dry type transformer in place of 2x1000 KVA oil type transformers at new location is in basement due to space constraint

- 15 nos. HTVC panel board comprising of 2 nos. in-coming panels 1250 amps capacity.. One no. bus coupler 1250 amps and 12 nos. out-going panels.

- 3 nos. ACB two-tier LT. Panel board comprising 1 no. 2500 amps + 800 amps(I/C + O/G) and 2 nos. 800amps + 800 amps (O/G + O/G)

- One no. dry type battery tripping unit.

- 2X400  mm2  HT XLPE Cable from proposed 33 KV sub-station for each I/C panel.

- Existing cables shall be extended and terminated in proposed sub-station.

PART ‘B’

- 400/3-½ C LT. XLPE Cable and st. th. Joints are  taken for extending the  cables from existing sub-station to proposed sub-station.

- G.S Pillar no. 49,49A & 65 are proposed to be fed through proposed Electric Substation  in Handloom Complex.

- G.S Pillar no. 37,38,39,64 & 64E are proposed to be fed through  proposed big  size G.S pillar near proposed unitized sub-station near Scindia House through  LT XLPE Cable 400  mm2 /3-½ C.

- New proposed big size  GS Pillar near Scindia House to be connected from proposed 2 nos. unitized sub-station Scindia House by 2X400 sq.mm/3-½ C LT XLPE Cable.

(5)	Financial implications : Financial implications in the proposal is anticipated to be Rs.1,45,85,000/- (gross) and Rs.1,45,02,500/-(net).

(6)	Implementation schedule: Six months

(7)	Comments of the Finance Deptt. on the subject :

Finance Deptt. vide Dy. No. 300/Finance/R-Elect. Dated 21-02-2011 have concurred in the estimate with no further comments.

(8)	Comments of the Deptt. on the Comments of the Finance  Deptt. : 	NIL

(9)	Legal implication of the Project : - No legal implication is involved.

(10)	Details of previous Council Resolution :	NIL

(11)	Comments of  Law Deptt. :  NIL

(12)	Comments of the Deptt. on the comments of Law Deptt.: NIL

(13)	Certification by the Deptt. that all Central Vigilance Commission (CVC) guidelines have been followed : It is certified that all Central Vigilance Commission (CVC) guidelines have been followed in processing the case.

(14)	Recommendation  : The estimate amounting to Rs.1,45,85,000/- (gross) and Rs.1,45,02,500/-(net) for New proposed HT feeds for Shifting of Existing sub-station from ground floor to the proposed location in  basement of Handloom Complex at Janpath Lane,  New Delhi may be placed before the Council to accord administrative approval and expenditure sanction.

(15)	Draft Resolution : Resolved by the Council that Administrative approval and expenditure sanction is granted to the estimate amounting to Rs.1,45,85,000/- (gross) and Rs.1,45,02,500/-(net) for Shifting of Existing sub-station from ground floor to the proposed location in  basement of Handloom Complex at Janpath Lane,  New Delhi.

COUNCIL SECRETARIAT

Resolved by the Council to accord administrative approval and expenditure sanction to the estimate amounting to Rs.1,45,85,000/- (gross) and Rs.1,45,02,500/- (net) for Shifting of Existing sub-station from ground floor to the proposed location in the basement of Handloom Complex at Janpath Lane,  New Delhi.