ITEM NO. 20 (B-20)

(1) Name of the work :	Installation of 2 x 990 KVA unitized substations in Palika Niwas, Lodhi Colony, New Delhi.

(2) Name of the Department  :  Electricity Department.

(3) Brief History of the case :

E.E.(M/S) has informed that the existing only substation in Lodhi Colony, Block-5 is provided with 2x1000 KVA transformers. These transformers are almost 100% loaded and the stand-by capacity has completely been eaten up over the period of time. There are requests for installation of Electric Substation to meet the continuous increasing load demand in the area. The proposed substation will be required for meeting the additional load demand of the area. The existing substation in Lodhi Colony, Block-5 is provided with 2x1000 KVA transformers. Presently, area is fed from Substation Aliganj No.1. There is sanctioned scheme under execution by E.E.(C-I) for augmentation of existing 1000 KVA transformer by 1500 KVA transformer in addition to above proposal as the load demand of the area is increasing continuously.

(4)  Detailed proposal on the Project :

In this connection, it was decided to install 2 x 990 KVA unitized substations and same was approved by the then C.E.(E)II  dated 26-5-2006.  The site was inspected alongwith the officers of Architect Deptt. and  a  suitable  site for the installation of 2 x 990 KVA unitized substations was finalized.

The feasibility has been worked out for providing HT feeds  to the proposed unitized substations  in Palika Niwas Lodhi Colony.  E.E.(M/S) proposed that the existing HT feed between Electric Substation Aliganj No. 1 & Electric Substation Lodhi Colony may be augmented to 300 sq.mm/3C and laid through proposed unitized substations 1 & 2 at Palika Niwas and same was approved by A.C.E.(E)I  dated 19-8-2008.

(5)	Financial implications : Financial implications in the proposal is anticipated to be Rs.68,86,500/-. The expenditure will be charged to the budget Head: E-4-1, for which budget provision will be kept suitably in the B.E. 2009-10.

(6)	Implementation schedule:  Eight months.

(7)	Comments of the Finance Deptt. on the subject :

Finance Deptt. vide Dy. No. 2618/Finance dated 24-10-08 has concurred  in the estimate amounting to Rs. 68,86,500/- (Rupees Sixty eight lakhs eighty six thousand and five hundred only) for the work of  Installation of 2 x 990 KVA unitized substations in Palika Niwas, Lodhi Colony, New Delhi. as per estimate prepared by 11 KV Planning division and recommended by A.C.E.(E)II subject to the following conditions :

- Availability of funds.

- Approval of the competent authority.

- Correctness of information and data submitted by the department.

- Codal provisions shall be adhered.

- Certification that the lowest market rates have been taken into account in respect of items analyzed on market rates.

- It may be certified that the proposed augmentation is necessary to meet the additional load requirement.

(8)	Comments of the Deptt. on comments of Finance Deptt.

- Funds shall be available.  A provision of Rs. 66 lacs in B.E. 2009-10 under budget head E-4-1 is kept.

- Approval of competent authority is being obtained.

- The information and data submitted has been  verified.

- All codal provisions have been adhered.

- Lowest market rate have been taken into account.

- It is certified that  proposed  augmentation is necessary to meet the additional load requirement.

(9)	Legal implication of the Project : No legal implication is involved.

(10)	Details of previous Council Resolution :	NIL

(11)	Comments of  Law Deptt. :  No comments.

(12)	Comments of the Deptt. on the comments of Law Deptt. :  N.A.

(13)	Certification by the Deptt. that all Central Vigilance Commission (CVC) guidelines have been followed :

It is certified that CVC guidelines have been followed while processing the case.

(14)	Recommendation : The estimate amounting to Rs.68,86,500/-for Installation of 2 x 990 KVA unitized substations in Palika Niwas, Lodhi Colony, New Delhi may be placed before  the Council  to accord Administrative Approval and Expenditure Sanction.

(15)	Draft Resolution : Resolved by the Council that Administrative Approval and Expenditure Sanction is granted to the estimate amounting to Rs.68,86,500/- for Installation of 2 x 990 KVA unitized substations in Palika Niwas, Lodhi Colony, New Delhi.

COUNCIL’S DECISION

Resolved by the Council to accord Administrative Approval and Expenditure Sanction to the estimate amounting to Rs.68,86,500/- for installation of 2x990 KVA unitized substations in Palika Niwas, Lodhi Colony, New Delhi.