ITEM NO. 20 (B-17)

l. 		Name of the Project:- Augmentation of transformation capacity at S/S Nirman Bhawan (Replacement of third transformer)

2. 		Name of the Department Concerned:- Electricity Department

3. 		Brief history of the project:-

S/S Nirman Bhawan caters to the electrical load demand of important buildings, such as Rashtrapati Bhawan, North Block, South Block, Udyog Bhawan, Vayu Bhawan, Parliament House etc.. The load of these buildings and the adjoining area in general is increasing day by day. As such the transforming capacity of this sub-station is required to be enhanced. However due to space constraints i.e. non availability of additional land, it is not possible to add more transformer. As such it had been proposed to replace the existing 33/11KV, 10 MVA transformers with higher capacity transformers of 12.5/16 MVA to meet the growing load demand. This enhancement of transformer capacity will also enable NDMC to utilize the full capacity of 33KV feeders coming from I.P. Sub-Station and Park Street S/S.

There are three numbers Transformers of 33/11KV, 10MVA each at S/S Nirman Bhawan. These transformers were installed in the year 1964, 1967 and 1973 by the erstwhile DESU. As per the Gazette of India, the useful life of the transformer is 25 years. Thus all the three transformers have already served their useful life and can not be relied upon and need replacement. The scheme for augmentation of the transformer capacity at S/S Nirman Bhawan has already been technically cleared by CEA under Xth Five Year Plan vide letter No. DPD/UT/312(DEL)/2003/419 dt. 15.12.03.

A meeting of the Technical Sub Committee was held in the Chamber of the CE(E)-I on 22.09.05 to discuss the augmentation of the transforming capacity at S/S Nirman Bhawan. It was decided to replace the existing 33/11KV, 10MVA transformers with 12.5/16 MVA transformers. The estimate for replacement of three transformers was processed. However, the then CE(E)-I had some reservation and decided that the case for replacement of only two transformers be processed first.

4. 		Detailed proposal on the Project:-

The work of replacement/augmentation of two transformers at S/S Nirman Bhawan has been outsourced to M/s Power Grid. The transformers for the S/S Nirman Bhawan have to be specially designed to accommodate in the existing available space due to space constraints. It will not be easy to get the third transformer of identical special design at later date. As such, when the two transformers are being replaced, the third existing 10 MVA transformer shall also be replaced with higher capacity of 12.5/16 MVA. The replacement of third transformer shall enhance the transforming capacity, which in any case would be needed to meet the ever increasing load of the VVIP area. It is therefore proposed to get done the replacement work of third transformer from M/s PGCIL. This enhancement of transformer capacity will also enable NDMC to utilize the full capacity of 33KV feeders coming from I.P. Sub-Station and Park Street S/S.

5. 		Financial implications of the proposed project:-

The estimated cost for replacement/augmentation of third power transformers is        Rs.1,45,46,500/-(Gross) and Rs.1,45,05,600/-(Net) chargeable to the head of A/c E-4.1.

6.	Implementation schedule with timeliness for each stage including internal processing:-

The scheme has been outsourced to M/s Power Grid Corporation of India Limited for turnkey execution and as per MOU completion time is 24-30 months.

7.		Comments of the Finance Deptt. on the subject:-

The Finance Deptt. has concurred to the  proposed estimate vide diary No. 1668/Finance dated 7/08/09 subject to:-

- Approval of Competent Authority

- Availability of funds

- The work would be got executed after adhering the codal provisions

- Since the proposed replaced transformer is still in good working condition. The same must be used elsewhere in the larger interest of the Council

8.		Comment of the Deptt. on comments of Finance Deptt.:-

- Approval of the competent authority i.e. Council is being sought.

- Rs. 2.50 Crores has been kept in the BE 2009-10. The budget shall be suitably revised in RE-2009-10 and subsequent years as per future requirement.

- The codal provisions would be adhered to.

- The existing transformer has already served its prescribed useful life. However, the dismantled transformers shall be utilized as per requirement of the Deptt.

Finance Deptt. has seen the replies and has offered no further comments.

9.		Legal implication of the Project:-  	No legal implication  involved.

10.	Details of previous Council resolution:- The A/A & E/S to the  estimate for replacement/augmentation of two nos. Power Transformers at this S/S was accorded by Council vide Reso. No.    7(B-14) dated 13.02.06

11.		Comments of the Law Deptt. on the project:- 	NIL

12.		Comments of the Deptt. on the comments of Law Deptt.:-  NIL

13. 		Certificate on CVC guidelines: -

All CVC guidelines shall be adhered to while processing the case.

14.		Recommendation of Deptt. :-

The estimate amounting to Rs.1,45,46,500/-(Gross) and Rs.1,45,05,600/-(Net) for replacement/augmentation of third power transformers at S/S Nirman Bhawan, is placed before the Council to accord administrative approval and expenditure sanction. Since the work is of urgent nature and replacement work of two transformers has already been outsourced to M/S PGCIL, approval is solicited to get  done the replacement of third transformer work from M/s PGCIL as additional quantity. Also accord approval to take further action in anticipation to confirmation of the Minutes of Council Meeting.

15.		Draft Resolution :-

Resolved by the Council that Administrative approval & expenditure sanction is granted to the estimate amounting to Rs.1,45,46,500/-(Gross) and Rs.1,45,05,600/-(Net) for replacement/augmentation of third power transformers at S/S Nirman Bhawan.  Since the work is of urgent nature and replacement work of two transformers has already been outsourced to M/S PGCIL, approval is accorded to get done the replacement of third transformer work from M/s PGCIL as additional quantity. Further approval is accorded to take action in anticipation to confirmation of the Minutes of Council Meeting

COUNCIL’S DECISION

Resolved by the Council to accord administrative approval & expenditure sanction to the estimate amounting to Rs.1,45,46,500/- (Gross) and Rs.1,45,05,600/- (Net) for replacement/augmentation of third power transformers at S/S Nirman Bhawan.

Since the work is of urgent nature and replacement work of two transformers has already been outsourced to M/S PGCIL, approval is accorded by the Council to get the replacement of third transformer done by the M/s PGCIL as additional quantity.

It was also decided by the Council that the department would ensure the quality of the transformer being purchased and also a letter to this effect be sent to M/s. PGCIL for ensuring the quality of the product.

It was also resolved that further action in the matter be taken in anticipation of confirmation of the minutes by the Council.

Resolution moved by Shri karan Singh Tanwar, Member, NDMC U/s 23 of NDMC Act, 1994 regarding providing booking of open ground/parks and water tanker/trolley for religious functions free of charge.

Some important institutions/buildings of all religious faiths i.e. Hindu, Sikh, Christian, Muslim etc., are situated in NDMC area. Religious functions are organized by people belonging to all these faith, which are attended by lakhs of believers. These institutions are largely headed/managed by senior citizens, who have to visit the offices in connection with booking of open ground/parks to organize their functions and/or for booking of water tanker/trolley for the event.

It shall be of paramount help to the believers of all faiths if the land/park is booked for religious functions without any booking charge and water for use of devotees is also provided free of cost on humanitarian grounds, as a welfare measure.

In view of the above, it is resolved that the Council may provide booking of open ground/parks of religious functions without any booking charge and also provide water trolley/tanker free of cost on humanitarian grounds, as a welfare measure.

Council’s Decision

It was decided by the Council that a report in this matter be placed before the Council meeting by the concerned department.

(GYANESH BHARTI)					 	( PARIMAL RAI )

# SECRETARY						  CHAIRPERSON