ITEM NO. 09 (B-13)

(1) Name of the Project :	Installation of  Two 990 KVA Unitized substations, adjacent to NDMC Fire Control Room and  temple near Lok Nayak Bhawan Khan Market, New Delhi.

(2) Name of the Department  :  Electricity (Planning)

(3) Brief History of the Project :

There is an Electric Substation in the basement of Lok Nayak Bhawan having 5 x 1000 KVA transformers feeding the load to the various offices/shops in the building as well as outside load in the adjoining areas. The load requirement in Khan Market area  is increasing day by day and is not feasible to meet the same from the existing Electric Substation in Lok Nayak Bhawan.  CA, NDMC  approved plot of size 15 x 6 meters  adjacent to NDMC Fire Control Room and  temple near Lok Nayak Bhawan Khan Market, New Delhi for the installation of two 990 KVA unitized substations.

(4)  Detailed proposal on the Project :  CA, NDMC has approved  plot  of 15 x 6 meters size adjacent to NDMC Fire Control Room and  temple near Lok Nayak Bhawan Khan Market, New Delhi for the installation of two 990 KVA unitized substations.  There are a number of Govt. offices like; C.G.A., CBI, CBDTD, OPT etc. being maintained by CPWD besides other Govt./semi-Govt. offices etc.  S.E., CPWD has requested vide various letters to increase the  load to 1800 KW as the load demand of various offices is increasing day by day due to installation of Acs, computers and other modern gadgets .  E.E.(D/S) has mentioned in letter dated 13-10-06 that the existing load  of various offices in Lok Nayak Bhawan is 432.62 KW as such there is an additional requirement of 1367.38 KW  which cannot be met from the existing Electric Substation in Lok Nayak Bhawan without diverting the existing LT feeders feeding supply in the adjoining areas as the Electric Substation is running to its full capacity.

It is the prime responsibility of Council to provide uninterrupted power supply to its various consumers.  The proposed unitized substations shall facilitate uninterrupted power supply and shall meet additional load requirement of various consumers in the adjoining areas as the number of connections as well as the load requirement is increasing day by day.  The benefit of the proposed system is difficult to express in monitory terms.  However the cost incurred in the proposed system shall be beneficial in terms of efficient power distribution and recovered gradually by revenue increase as a result of sanction of additional load.

The following has been proposed in the estimate :

- 2 Nos. 990 KVA unitized substation.

- HT feed of size 300 sq.mm/3C.

- LT XLPE cable of size 400 sq.mm/3-1/2C.

- Pillar big size complete.

Accordingly an estimate amounting to Rs. 1,22,39,500/-  has been framed for Installation of  two 990 KVA Unitized substations,  adjacent to NDMC Fire Control Room and  temple near Lok Nayak Bhawan Khan Market, New Delhi to meet the load in the Khan Market area and also diverting the outside load being fed from Electric Substation Lok Nayak Bhawan to the proposed unitized substations by installing GS Pillars.  The expenditure shall be charged to the head of account E-4-1.

(5)	Financial implications of the proposed project : Accordingly an estimate amounting to Rs. 1, 22,39,500/-  has been framed for Installation of  two 990 KVA Unitized substations, adjacent to NDMC Fire Control Room and  temple near Lok Nayak Bhawan Khan Market, New Delhi to meet the load in the Khan Market area and also diverting the outside load being fed from Electric Substation Lok Nayak Bhawan to the proposed unitized substations by installing GS Pillars.  The expenditure shall be charged to the head of account E-4-1  for which a provision of Rs. 10 lacs during R.E. 2006-07 & Rs. 40 Lacs during B.E. 2007-08 was proposed.  During the finalization of R.E.2006-07 & BE 2007-08, the proposed amounts were reduced to Rs.1 lac & Rs. 20 lacs respectively and it was informed that the same shall be increased after the approval of the estimate.

(6)	Implementation schedule with timeliness for each stage including internal processing :

| i) Approval of scheme by Council | July, 2007 |
| --- | --- |
| ii) Technical sanction of the estimate | August, 2007 |
| iii) Issue of estimate to Construction Division for execution | August, 2007 |
| iv) Preparation of draft NIT | September, 2007 |
| v) Call of tenders | September, 2007 |
| vi) Award of work including opening of tenders, negotiation with the tenderer etc. | November, 2007 |
| vii) Completion of work | February, 2008 |

(7)	Comments of the Finance Deptt. on the subject :

The Finance Deptt. has concurred to the proposed estimate subject to

- Availability of funds.

- Approval of the competent Authority.

- Correctness of information and data submitted by the Deptt.

- Codal provision be adhered to while execution of the work.

- The Project Report be prepared in accordance with the format given in the Standing Order No. 7/2003-04 dated 2-9-03 before seeking approval of the Competent Authority.

- After execution of the work the matter for enhancement of load of the consumers be taken up.

- The credit sheet be added, if any.

- The time for completion of work be brought on record before taking A/A of Competent Authority.

(8)	Comments of the Deptt. on comments of Finance Deptt.

- Funds are available. Provision of Rs. 10 lacs during R.E. 2006-07 & Rs. 40 Lacs during B.E. 2007-08 was proposed.  During the finalization of R.E.2006-07 & BE 2007-08, the proposed amounts were reduced to Rs.1 lac & Rs. 20 lacs respectively and it was informed that the same shall be increased suitably after the approval of the estimate.

- Necessary approval is being sought from the competent authority.

- Information and data are correct.

- The work would be executed by the executing division as per the Codal provision.

- Project report has been prepared and placed in the file.

- The matter for enhancement of load of the consumers will be taken up.

- This being a new substation, Credit sheet is not required.

- Time for completion of work : Four months after award of work i.e.  February, 2008.

(9)	Legal implication of the Project : No legal implication is involved.

(10)	Details of previous Council Resolution :	N.A.

(11)	Comments of the L.A. & C.A. on the project :

L.A. has referred the case to C.A. with the remarks that:

“The proposal is to meet additional requirement of Khan Market.  It is presumed that land use permits installation of 990 KVA unitized substations.  CA may please confirm it the units are not for Lok Nayak Bhawan exclusively”.

C.A. has observed that :

“The records reveal that while Architect Deptt. was requested to select a suitable site, it was stated by the Electricity Deptt. that establishment of a unitized sub station in Lok Nayak Bhawan Complex is to meet up the required load of Lok Nayak Bhawan only and the site for unitized substation shall be in ground floor.  Accordingly the proposed site was suggested by Architect Deptt.  ESS/USS can be installed in any land irrespective of its land use.  However, if the USS in question is not for Lok Nayak Bhawan only then it may be installed some other location like near the Public Convenience opposite to Prithvi Raj Market or at the back/rear side of Prithvi Raj Market, Electrical Deptt. may also explored whether USS could be installed in the basement or not.  Elect. Deptt. may also furnish the exact size of USS for assessment of space required to install USS.”

(12)	Comments of the Deptt. on the comments of L.A. & C.A. :

The clarifications are as under :

CA, NDMC had earlier approved  plot  of 15 x 6 meters size adjacent to NDMC Fire Control Room and  temple near Lok Nayak Bhawan Khan Market, New Delhi for the installation of two 990 KVA unitized substations.

The other location for installing the unitized substations, suggested by C.A., are not found suitable being not at load centre locations and will unnecessarily increase the estimated cost.

The proposed 2 Nos. 990 KVA unitized substations are to be installed for diverting the outside load being fed from Electric Substation Lok Nayak Bhawan  meeting the load requirement of Khan Market area.   New sub-stations will ease the load on existing substation in the basement of Lok Nayak Bhawan.  NDMC will be then in a position to meet additional load demand of offices in Lok Nayak Bhawan.

The proposed unitized substations cannot be installed in the basement due to non availability of space in the substation.

Two unitized substations can be accommodated in the earmarked area of 15 x 6 mtrs.

(13)	Recommendation : The case may be noted to the Council for sanction of estimate amounting to Rs. 1,22,39,500/- (Rupees One Crore Twenty two lakh thirty nine thousand five hundred only) for Installation of  two nos. 990 KVA Unitized substations adjacent to NDMC Fire Control Room and  temple near Lok Nayak Bhawan Khan Market, New Delhi and also to accord administrative approval and expenditure sanction to the estimate.

(14)	Draft Resolution : Resolved by the Council that estimate amounting to Rs. 1,22,39,500/- (Rupees One Crore Twenty two lakh thirty nine thousand five hundred only) is sanctioned and A/A & E/S accorded  for Installation of  two nos. 990 KVA Unitized substations adjacent to NDMC Fire Control Room and  temple near Lok Nayak Bhawan Khan Market, New Delhi.

COUNCIL’S DECISION

Resolved by the Council that administrative approval and expenditure sanction to the estimate amounting to Rs.1,22,39,500/- is accorded for installation of two nos. 990 KVA Unitized Sub-stations adjacent to NDMC Fire Control Room and Temple near Lok Nayak Bhawan, Khan Market, New Delhi.