ITEM NO. 14 (B-8)

1. Name of the Project- ESTABLISHING 33KV INDOOR S/S AT THE PLACE OF OLD 33KV S/S CONNAUGHT PLACE & AUGMENTATION OF ITS TRANSFORMER CAPACITY.

SH:		    Revalidation of sanction to the above estimate.

2. Name of the Department concerned-   Electricity (Planning)

3. Brief History of the Project- The existing 33KV S/S at Connaught Place is an outdoor type S/S. It is proposed that a new 33KV S/S building shall be constructed at the place of old S/S building which will accommodate 33KV and 11KV indoor switchgears besides site offices of Distribution (North) and Maintenance (North) Divisions, which are presently located in the temporary structure of old building and Ist floor of the existing building.

The load demand in the area is going to increase due to redevelopment of the Connaught Place.  The existing 2 Nos. transformer of capacity 12.5/15MVA and 16/20MVA shall not be able to meet this growing load demand as such it has been proposed to install one more transformer of 33/11KV, 12.5/16MVA capacity to accommodate in the available space.  The scheme was cleared by the CEA   as part of 10th Five-year plan.  But the scheme could not be implemented due to change of conceptual plans on basis of norms/permissible FAR.

The Chairperson desired during the review meeting of Electrical estimate held on 9.1.07 that cases where the validity has expired and no work has taken place, either all such cases be put up afresh for revalidation or should be closed if not required.

4. Detailed proposal on the Project- It has been proposed to augment the transforming capacity of S/S Connaught Place from existing 35MVA to 51MVA by installing an additional 33/11KV transformer of 12.5/16MVA.  The 33KV OCB type switchgear installed in out-door yard have served their useful life of 25 years. In place of existing 33KV OCBs, 33KV indoor GIS panel board having 11 panels has been proposed to be installed.  The following has been proposed in the estimate

- 33/11KV transformer 12.5/16 MVA – 1 No.

- 33KV SBB, indoor type GIS panel boards - 11 Nos.

- 11KV SBB, indoor type SF6/Vacuum panel board – 10Nos.

The cost of 3 nos. 33KV GIS panels is proposed to be charged to Head of A/C  E-3 (Replacement work) and balance 8 nos. 33KV GIS panels have been charged to Head of A/C E-4-1 ( plan work).  The new Power Transformer shall be installed at the place of existing 33KV OCBs in the out-door yard.

5. Financial implications of the proposed Project-   An estimate amounting to Rs. 495.13 lacs (G) and Rs. 494.29 Lacs (N) was framed for upgradation of the S/S which includes the cost of new building as detailed below-

REPLACEMENT WORK (HEAD OF A/C E-3)

i) Cost of new building	Rs.  63.85 lacs

ii)Cost of equipment’s 	Rs. 220.67 lacs

iii)Less credit for old equipment                      	 Rs.     0.84 lacs

PLAN WORK (HEAD OF A/C E-4-1)

i) Cost of additional equipment’s 	Rs. 210.60 lacs

Total	Rs. 495.13 lacs(G)

Rs. 494.29 lacs(N)

The estimate will be revised as per actual basis after execution of the work. A budget provision of Rs. 40.00 lacs has been kept during the financial year 2007-08 and suitable budget provision will be made under the respective head of accounts in different financial years.

6. Implementation schedule with timeliness for each stage including internal processing-

i) Approval of scheme by Council 	July 2007

ii) Issue of estimate to construction

Division for execution	August 2007(Revalidation)

iii) Preparation of draft NIT(Elect.)	September 2007

iv) Call of tenders (Elect.)	  October 2007

v) Award of work including

opening of tenders, negotiation

with the  tenderer etc.		     		Feb.  2008

vi) Completion of work	 December 2009

7. Comments of Finance Deptt. on the subject-

Finance Deptt. has concurred to the proposal to revalidate the sanction of the estimate amounting to Rs. 495.13 lacs (G) and Rs. 494.29 lacs (N) for establishing 33KV Indoor S/S at the place of old  33KV S/S Connaught Place and augmentation of its transformer capacity subject to the following conditions-

- Approval of competent Authority

- Availability of funds

- Correctness of information and data submitted by the department.

- Codal provisions are adhered during the execution of the work.

5)	The revised estimate be got concurred in from Finance Department before awarding the work.

8. Comments of the Deptt. on comments of Finance Deptt.-

Observations of the Finance Deptt. are clarified as under:-

  - Approval of the competent authority is being obtained.

  - Budget provision of Rs. 40.00 lacs exist during 2007-08, however suitable provision will be kept in subsequent financial years.

  - Information & data provided are correct.

  - The work would be executed by the executing division as per codal provisions.

  - Necessary concurrence of the Finance would be obtained by the executing division before awarding the work.

9.Legal implication of the Project- No legal implication is involved.

10.Details of previous Council Resolution-  Item No. 3(xxviii) dated 28.1.2002.

11.Comments of the Law Deptt. on the Project-  N.A.

12.Comments of the Deptt. on the comments of the Law Deptt.- Nil

13.Recommendation- The case may be noted to the Council to revalidate A/ A &

E/S to the estimate amounting to Rs. Rs.495.13 lacs (G) and Rs. 494.29 lacs(N) for establishing 33KV Indoor S/S at the place of old 33KV S/S Connaught Place & augmentation of its transformer capacity, as concurred by the Finance.

14.Draft Resolution-   Resolved by the Council that A/A & E/S to the estimate amounting to Rs Rs.495.13 lacs (G) and Rs. 494.29 lacs(N) for establishing 33KV Indoor S/S at the place of old 33KV S/S Connaught Place & augmentation of its transformer capacity is revalidated.

COUNCIL’S DECISION

Resolved by the Council that administrative approval and expenditure sanction to the estimate amounting to Rs Rs.495.13 lacs (Gross) and Rs. 494.29 lacs(Net) for establishing 33KV Indoor S/S at the place of old 33KV S/S Connaught Place & augmentation of its transformer capacity is revalidated.

Further resolved by the Council that the project be completed within the time frame mentioned in the proposal.